                                                                                                                                              Phone     : 2265-0001 (3 Lines)

                                                                                                                                              Fax          : (033) 2265-8537

                                                                                                                                              Website   :  www.gluconatehealth.com
                                                                                                                                              E-mail      : ghlmd@rediffmail.com  

	[image: image5.jpg]



	     Gluconate Health Limited

               (A  GOVERNMENT OF WEST BENGAL UNDERTAKING)

                    Registered & Head Office: 2, DURGA CHARAN DOCTOR LANE,  KOLKATA – 700 014 


[image: image5.jpg]



TENDER NO : GHL/ELECT-  02 /21-22          Dt. 15.09.21
LAST DATE OF SUBMISSION : 01.10.21
 S.O.W

 Name of Work: Supply, fitting & fixing of 630A, 440V, 50 HZ PDB MCCB Panel board in old building at GHL factory,  Dumdum Cantonment
	Sl.
no.
	Description of Works
	Qnty.
	Unit

	1
	Disconnection and dismantling of the old damaged composite panel from the wall part by part as per direction of E.I.C
	1
	Job.

	2
	Design, drawing, S&D of 440V, 3 Ph, 630A, 50 HZ PDB MCCB Panel fabricated from 2/1.6mm (Load Bearing/non load bearing) of size 1850mm x 1925mm x 500mm CRCA Sheet enclosure, paint shad powder coating RAL – 7032 and size of BBC Ph. 50mm x 10mm x36” and natural bar 40mm x 6mm x 36” including earthing attachment. Following materials are include inside the PDB panel.

INCOMING

a) 630A, 440V, 3 Ph., 4 Pole MCCB

b) Rotary Handle MCCB

c) 630A Spreader Terminals

d) 630A 4-Pole C/O Switch

e) LED Indication Lamp

f) 0 – 500V volt meter of size (96mm x 96mm)

g) Volt Selector Switch

h) 600/5 A Ammeter of size (96mm x 96mm)

i) Am- Selector Switch 

j) 600/5A C.T. Coil

k) 6A, SPMCB

l) 4-Pole Power Connector 
	1

1

1

1

1

6

1

1

1

1

3

6 

12
	Job.

No.

Set.

Set.

No.

Nos.

No.

No.

No.

No.

Nos.

Nos.

Nos.

	3
	OUTGOING

a) 400A, 4-Pole MCCB                                                          -

b) 400A, 4-pole MCCB Rotary Handle

c) 400A, 4-pole MCCB spreader Terminals

d) 200A, 4-pole MCCB
e) 200A, 4-pole MCCB Rotary Handle
f) 200A, 4-pole MCCB spreader Terminals

g) 100A, 4-pole MCCB

h) 100A, 4-pole MCCB Rotary Handle
i) 100A, 4-pole MCCB spreader Terminals

j) 250A, 4-way terminal
	1

1

1

1

1

1

8

8

8

8
	No.

No.

Set.

No.

No.

Set.

Nos.

Nos.

Sets

Nos.

	4
	Supply of Copper Conductor cable single core 1100v, flexible unarmored conforming to IS:694 of Havels make size are mentioned below.

a) 6 sq. mm.                                                                       

b) 10 sq. mm.

c) 16 sq. mm.

d) 25 sq. mm.
	25

30

25

20


	Mts.

Mts.

Mts.

Mts.

	5
	Supply of Copper Bar of Size

a) 40mm x 10mm x30’       -------            06 kg.

b) 40mm x 6mm x 10’        -------            08 kg.

c) 40mm x 3mm x 9’          -------            05 kg.

d) 25mm x 5mm 10’           -------            07 kg.
                                                           26 kg.

(Ref: Analyses Enclosed)


	26
	Kg.

	6
	Installation, testing & commissioning the complete 630A and 400A DG Panel at the old building in existing wall at GHL Factory premises.
	1
	Jobs.

	7
	Earthing with 50 mm dia GI Pipe 3.64mm thick x 3.04 mts. Long and 1 x 4 SWG GI (Hot Dip) wire (4 mts. long) 13mm dia x 80mm long GI bolts, double nuts, double washers including S&F 15mm dia GI pipe protection (1 mts long) to be filled with bitumen partly under the ground level and partly above ground level driven to an average depth of 3.65 mts. Below the ground level.

a) By TATA- Medium GI Pipe

	2
	Jobs.

	8
	Supplying & fixing compression type gland complete with brass gland, brass ring & rubber ring for dust & moisture proof entry of XLPE/PVC armored cable.

a) 3[image: image2.png]


 core 300 sq.mm.


	3
	Nos.

	9
	Finishing the end of following XLPE/PVC armored cables by crimping method including S&F solderless rocket (Dowels make) tapes, anticorrosive paste & jointing materials.

a) 3[image: image4.png]


 core 300 sq.mm.
	3


	Sets.


For Gluconate Health Limited

Managing Director


